## Sheet1
sewage flow = 2.5 ft/s
Peak factor= 4
Sr. No. | 1 | 2 | 3 | 4 | [5 empty] | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
| Sewer. No | Sewer Name |  | Length | [5 empty] | Demand Flow |  |  | Avg Daily Sewage flow(Qavg) | Infiltration | Peak sewage flow | Storm sewage | Design Flow(Qd) | Peak design velocity(Vf) | Diameter |  | Diameter difference | Thickness of pipe | Slope | Qfull | Qd/Qfull | d/D | d | V/Vfull | Va | Fall | Ground Level |  | Invert Level |  | Status
|  | From | To |  | Avg Online Sewage flow | Infiltration | Design flow | Equivelant pop | Per capita flow | 5: Online; 6: Previous; 7: Total; 14: Calculated; 15: Provided; 26: U/E; 27: L/E; 28: U/E; 29: L/E
|  | MH | MH | ft | gpm | gpm | gpm |  | gpm | gpm | gpm | gpm | cusec | cusec | cusec | cusec | cusec | ft/sec | inch | inch | inch | ft | ft | cusec | cusec/cusec | ft/ft | ft |  | ft/sec | ft | ft | ft | ft | ft
1 | 28-29 | 28 | 29 | 268 | 3.2 | 0.32 | 25.92 | 84 | 0.30857 | 9 | 0 | 9 | 0.0071296 | 0.00071296 | 0.028518 | 0.028518 | 0.05775 | 2.5 | 2.058 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.052287 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.1881 | 100 | 100 | 96.1042 | 94.916 | frequent cleaning/flush tank
2 | 29-30 | 29 | 30 | 161 | 3.5556 | 0.35556 | 28.8 | 91 | 0.31648 | 10 | 9 | 19 | 0.015051 | 0.0015051 | 0.060206 | 0.060206 | 0.12192 | 2.5 | 2.9902 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.11038 | 0.25 | 0.1875 | 0.7 | 1.75 | 0.71376 | 100 | 100 | 94.916 | 94.2023 | Period flushing
3 | 30-31 | 30 | 31 | 156 | 3.2 | 0.32 | 25.92 | 78 | 0.33231 | 9 | 25 | 34 | 0.026934 | 0.0026934 | 0.10774 | 0.10774 | 0.21817 | 2.5 | 4 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.19753 | 0.3 | 0.225 | 0.725 | 1.8125 | 0.69159 | 100 | 100 | 94.2023 | 93.5107 | Period flushing
4 | 31-32 | 31 | 32 | 269 | 1.4222 | 0.14222 | 11.52 | 36 | 0.32 | 4 | 43 | 47 | 0.037232 | 0.0037232 | 0.14893 | 0.14893 | 0.30158 | 2.5 | 4.7029 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.27306 | 0.4 | 0.3 | 0.8 | 2 | 1.1926 | 100 | 100 | 93.5107 | 92.3181 | OK
5 | 32-33 | 32 | 33 | 278 | 3.5556 | 0.35556 | 28.8 | 91 | 0.31648 | 10 | 47 | 57 | 0.045154 | 0.0045154 | 0.18062 | 0.18062 | 0.36575 | 2.5 | 5.1791 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.33115 | 0.425 | 0.31875 | 0.8 | 2 | 1.2325 | 100 | 100 | 92.3181 | 91.0857 | OK
6 | 33-34 | 33 | 34 | 791 | 2.8444 | 0.28444 | 23.04 | 70 | 0.32914 | 8 | 57 | 65 | 0.051492 | 0.0051492 | 0.20597 | 0.20597 | 0.41708 | 2.5 | 5.5307 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.37763 | 0.45 | 0.3375 | 0.825 | 2.0625 | 3.5067 | 100 | 100 | 91.0857 | 87.579 | OK
7 | 34-35 | 34 | 35 | 487 | 2.4889 | 0.24889 | 20.16 | 63 | 0.32 | 7 | 123 | 130 | 0.10298 | 0.010298 | 0.41193 | 0.41193 | 0.83416 | 2.5 | 7.8215 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.75526 | 0.725 | 0.54375 | 0.95 | 2.375 | 2.159 | 100 | 100 | 87.579 | 85.4199 | OK
8 | 35-36 | 35 | 36 | 487 | 5.6889 | 0.56889 | 46.08 | 142 | 0.32451 | 16 | 130 | 146 | 0.11566 | 0.011566 | 0.46263 | 0.46263 | 0.93683 | 2.5 | 8.2889 | 12 | 3 | 2 | 0.0030209 | 1.9635 | 0.47712 | 0.525 | 0.525 | 0.85 | 2.125 | 1.4712 | 100 | 100 | 85.1699 | 83.6988 | OK
9 | 36-38 | 36 | 38 | 305 | 4.6222 | 0.46222 | 37.44 | 114 | 0.32842 | 13 | 278 | 291 | 0.23052 | 0.023052 | 0.92209 | 0.92209 | 1.8672 | 2.5 | 11.7022 | 15 | 3 | 2.25 | 0.0022435 | 3.068 | 0.60862 | 0.625 | 0.78125 | 0.9 | 2.25 | 0.68427 | 100 | 100 | 83.4488 | 82.7645 | OK
10 | 38-50 | 38 | 50 | 207 | 2.8444 | 0.28444 | 23.04 | 70 | 0.32914 | 8 | 300 | 308 | 0.24399 | 0.024399 | 0.97596 | 0.97596 | 1.9763 | 2.5 | 12.0391 | 15 | 0 | 2.25 | 0.0022435 | 3.068 | 0.64418 | 0.625 | 0.78125 | 0.9 | 2.25 | 0.46441 | 100 | 100 | 82.7645 | 82.3001 | OK
11 | 50-51 | 50 | 51 | 562 | 5.3333 | 0.53333 | 43.2 | 591 | 0.073096 | 15 | 407 | 422 | 0.3343 | 0.03343 | 1.3372 | 1.3372 | 2.7078 | 2.5 | 14.0921 | 18 | 3 | 2.5 | 0.0017594 | 4.4179 | 0.61292 | 0.625 | 0.9375 | 0.9 | 2.25 | 0.98876 | 100 | 100 | 82.0501 | 81.0613 | OK
12 | 51-52 | 51 | 52 | 145 | 2.4889 | 0.24889 | 20.16 | 63 | 0.32 | 7 | 422 | 429 | 0.33984 | 0.033984 | 1.3594 | 1.3594 | 2.7527 | 2.5 | 14.2085 | 18 | 0 | 2.5 | 0.0017594 | 4.4179 | 0.62309 | 0.625 | 0.9375 | 0.9 | 2.25 | 0.25511 | 100 | 100 | 81.0613 | 80.8062 | OK
13 | 43-44 | 43 | 44 | 150 | 3.9111 | 0.39111 | 31.68 | 98 | 0.32327 | 11 | 0 | 11 | 0.008714 | 0.0008714 | 0.034856 | 0.034856 | 0.070583 | 2.5 | 2.2752 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.063907 | 0.075 | 0.05625 | 0.25 | 0.625 | 0.66499 | 100 | 100 | 96.1042 | 95.4392 | frequent cleaning/flush tank
14 | 44-45 | 44 | 45 | 168 | 3.2 | 0.32 | 25.92 | 84 | 0.30857 | 9 | 11 | 20 | 0.015844 | 0.0015844 | 0.063374 | 0.063374 | 0.12833 | 2.5 | 3.0679 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.11619 | 0.25 | 0.1875 | 0.7 | 1.75 | 0.74479 | 100 | 100 | 95.4392 | 94.6944 | Period flushing
15 | 45-48 | 45 | 48 | 453 | 2.1333 | 0.21333 | 17.28 | 56 | 0.30857 | 6 | 20 | 26 | 0.020597 | 0.0020597 | 0.082386 | 0.082386 | 0.16683 | 2.5 | 3.4979 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.15105 | 0.3 | 0.225 | 0.725 | 1.8125 | 2.0083 | 100 | 100 | 94.6944 | 92.6861 | Period flushing
16 | 48-49 | 48 | 49 | 220 | 4.6222 | 0.46222 | 37.44 | 348 | 0.10759 | 13 | 48 | 61 | 0.048323 | 0.0048323 | 0.19329 | 0.19329 | 0.39142 | 2.5 | 5.3578 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.35439 | 0.45 | 0.3375 | 0.825 | 2.0625 | 0.97532 | 100 | 100 | 92.6861 | 91.7108 | OK
17 | 49-50 | 49 | 50 | 371 | 3.9111 | 0.39111 | 31.68 | 97 | 0.3266 | 11 | 88 | 99 | 0.078426 | 0.0078426 | 0.3137 | 0.3137 | 0.63525 | 2.5 | 6.8255 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.57516 | 0.6 | 0.45 | 0.9 | 2.25 | 1.6447 | 100 | 100 | 91.7108 | 90.066 | OK
18 | 1-3 | 1 | 3 | 293 | 2.8444 | 0.28444 | 23.04 | 70 | 0.32914 | 8 | 0 | 8 | 0.0063374 | 0.00063374 | 0.02535 | 0.02535 | 0.051333 | 2.5 | 1.9403 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.046478 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.299 | 100 | 100 | 96.1042 | 94.8052 | frequent cleaning/flush tank
19 | 3-5 | 3 | 5 | 153 | 2.1333 | 0.21333 | 17.28 | 49 | 0.35265 | 6 | 8 | 14 | 0.01109 | 0.001109 | 0.044362 | 0.044362 | 0.089833 | 2.5 | 2.5668 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.081336 | 0.075 | 0.05625 | 0.25 | 0.625 | 0.67829 | 100 | 100 | 94.8052 | 94.1269 | frequent cleaning/flush tank
20 | 5-8 | 5 | 8 | 373 | 0.71111 | 0.071111 | 5.76 | 21 | 0.27429 | 2 | 22 | 24 | 0.019012 | 0.0019012 | 0.076049 | 0.076049 | 0.154 | 2.5 | 3.3607 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.13943 | 0.25 | 0.1875 | 0.7 | 1.75 | 1.6536 | 100 | 100 | 94.1269 | 92.4733 | Period flushing
21 | 8-36 | 8 | 36 | 553 | 3.2 | 0.32 | 25.92 | 77 | 0.33662 | 9 | 38 | 47 | 0.037232 | 0.0037232 | 0.14893 | 0.14893 | 0.30158 | 2.5 | 4.7029 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.27306 | 0.4 | 0.3 | 0.8 | 2 | 2.4516 | 100 | 100 | 92.4733 | 90.0217 | OK
22 | 9-12 | 9 | 12 | 287 | 1.0667 | 0.10667 | 8.64 | 28 | 0.30857 | 3 | 0 | 3 | 0.0023765 | 0.00023765 | 0.0095061 | 0.0095061 | 0.01925 | 2.5 | 1.1882 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.017429 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.2724 | 100 | 100 | 96.1042 | 94.8318 | frequent cleaning/flush tank
23 | 12-16 | 12 | 16 | 390 | 4.2667 | 0.42667 | 34.56 | 106 | 0.32604 | 12 | 15 | 27 | 0.021389 | 0.0021389 | 0.085555 | 0.085555 | 0.17325 | 2.5 | 3.5645 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.15686 | 0.3 | 0.225 | 0.725 | 1.8125 | 1.729 | 100 | 100 | 94.8318 | 93.1028 | Period flushing
24 | 16-19 | 16 | 19 | 223 | 2.1333 | 0.21333 | 17.28 | 57 | 0.30316 | 6 | 45 | 51 | 0.040401 | 0.0040401 | 0.1616 | 0.1616 | 0.32725 | 2.5 | 4.899 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.2963 | 0.4 | 0.3 | 0.8 | 2 | 0.98862 | 100 | 100 | 93.1028 | 92.1142 | OK
25 | 19-35 | 19 | 35 | 267 | 3.2 | 0.32 | 25.92 | 77 | 0.33662 | 9 | 132 | 141 | 0.1117 | 0.01117 | 0.44679 | 0.44679 | 0.90475 | 2.5 | 8.1457 | 12 | 3 | 2 | 0.0030209 | 1.9635 | 0.46078 | 0.525 | 0.525 | 0.85 | 2.125 | 0.80659 | 100 | 100 | 91.8642 | 91.0576 | OK
26 | 20-21 | 20 | 21 | 295 | 3.9111 | 0.39111 | 31.68 | 98 | 0.32327 | 11 | 0 | 11 | 0.008714 | 0.0008714 | 0.034856 | 0.034856 | 0.070583 | 2.5 | 2.2752 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.063907 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.3078 | 100 | 100 | 96.1042 | 94.7963
27 | 21-23 | 21 | 23 | 167 | 2.1333 | 0.21333 | 17.28 | 56 | 0.30857 | 6 | 11 | 17 | 0.013467 | 0.0013467 | 0.053868 | 0.053868 | 0.10908 | 2.5 | 2.8284 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.098765 | 0.075 | 0.05625 | 0.25 | 0.625 | 0.74036 | 100 | 100 | 94.7963 | 94.056
28 | 23-25 | 23 | 25 | 183 | 5.6889 | 0.56889 | 46.08 | 140 | 0.32914 | 16 | 28 | 44 | 0.034856 | 0.0034856 | 0.13942 | 0.13942 | 0.28233 | 2.5 | 4.5504 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.25563 | 0.4 | 0.3 | 0.8 | 2 | 0.81129 | 100 | 100 | 94.056 | 93.2447 | OK
29 | 25-34 | 25 | 34 | 128 | 3.2 | 0.32 | 25.92 | 84 | 0.30857 | 9 | 49 | 58 | 0.045946 | 0.0045946 | 0.18379 | 0.18379 | 0.37217 | 2.5 | 5.2244 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.33696 | 0.425 | 0.31875 | 0.8 | 2 | 0.56746 | 100 | 100 | 93.2447 | 92.6772 | OK
30 | 13-14 | 13 | 14 | 292 | 1.0667 | 0.10667 | 8.64 | 28 | 0.30857 | 3 | 0 | 3 | 0.0023765 | 0.00023765 | 0.0095061 | 0.0095061 | 0.01925 | 2.5 | 1.1882 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.017429 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.2945 | 100 | 100 | 96.1042 | 94.8096 | frequent cleaning/flush tank
31 | 14-15 | 14 | 15 | 193 | 3.9111 | 0.39111 | 31.68 | 99 | 0.32 | 11 | 3 | 14 | 0.01109 | 0.001109 | 0.044362 | 0.044362 | 0.089833 | 2.5 | 2.5668 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.081336 | 0.075 | 0.05625 | 0.25 | 0.625 | 0.85562 | 100 | 100 | 94.8096 | 93.954 | frequent cleaning/flush tank
32 | 15-16 | 15 | 16 | 209 | 1.4222 | 0.14222 | 11.52 | 36 | 0.32 | 4 | 14 | 18 | 0.014259 | 0.0014259 | 0.057037 | 0.057037 | 0.1155 | 2.5 | 2.9104 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.10457 | 0.25 | 0.1875 | 0.7 | 1.75 | 0.92656 | 100 | 100 | 93.954 | 93.0275 | Period flushing
33 | 40-41 | 40 | 41 | 450 | 1.0667 | 0.10667 | 8.64 | 28 | 0.30857 | 3 | 0 | 3 | 0.0023765 | 0.00023765 | 0.0095061 | 0.0095061 | 0.01925 | 2.5 | 1.1882 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.017429 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.995 | 100 | 100 | 96.1042 | 94.1092 | frequent cleaning/flush tank
34 | 41-42 | 41 | 42 | 432 | 2.1333 | 0.21333 | 17.28 | 56 | 0.30857 | 6 | 3 | 9 | 0.0071296 | 0.00071296 | 0.028518 | 0.028518 | 0.05775 | 2.5 | 2.058 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.052287 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.9152 | 100 | 100 | 94.1092 | 92.194 | frequent cleaning/flush tank
35 | 42-49 | 42 | 49 | 207 | 3.2 | 0.32 | 25.92 | 76 | 0.34105 | 9 | 9 | 18 | 0.014259 | 0.0014259 | 0.057037 | 0.057037 | 0.1155 | 2.5 | 2.9104 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.10457 | 0.25 | 0.1875 | 0.7 | 1.75 | 0.91769 | 100 | 100 | 92.194 | 91.2763 | Period flushing
36 | 46-47 | 46 | 47 | 437 | 3.5556 | 0.35556 | 28.8 | 91 | 0.31648 | 10 | 0 | 10 | 0.0079218 | 0.00079218 | 0.031687 | 0.031687 | 0.064166 | 2.5 | 2.1693 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.058097 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.9373 | 100 | 100 | 96.1042 | 94.1668 | frequent cleaning/flush tank
37 | 47-48 | 47 | 48 | 155 | 4.2667 | 0.42667 | 34.56 | 341 | 0.10135 | 12 | 10 | 22 | 0.017428 | 0.0017428 | 0.069712 | 0.069712 | 0.14117 | 2.5 | 3.2176 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.12781 | 0.25 | 0.1875 | 0.7 | 1.75 | 0.68716 | 100 | 100 | 94.1668 | 93.4797 | Period flushing
38 | 17-18 | 17 | 18 | 401 | 2.1333 | 0.21333 | 17.28 | 49 | 0.35265 | 6 | 0 | 6 | 0.0047531 | 0.00047531 | 0.019012 | 0.019012 | 0.0385 | 2.5 | 1.6803 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.034858 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.7777 | 100 | 100 | 96.1042 | 94.3264 | frequent cleaning/flush tank
39 | 18-19 | 18 | 19 | 202 | 6.7556 | 0.67556 | 54.72 | 168 | 0.32571 | 19 | 6 | 25 | 0.019804 | 0.0019804 | 0.079218 | 0.079218 | 0.16042 | 2.5 | 3.43 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.14524 | 0.25 | 0.1875 | 0.7 | 1.75 | 0.89552 | 100 | 100 | 94.3264 | 93.4309 | Period flushing
40 | 6-7 | 6 | 7 | 127 | 2.4889 | 0.24889 | 20.16 | 63 | 0.32 | 7 | 0 | 7 | 0.0055452 | 0.00055452 | 0.022181 | 0.022181 | 0.044916 | 2.5 | 1.815 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.040668 | 0.05 | 0.0375 | 0.25 | 0.625 | 0.56303 | 100 | 100 | 96.1042 | 95.5411 | frequent cleaning/flush tank
41 | 7-8 | 7 | 8 | 263 | 2.4889 | 0.24889 | 20.16 | 63 | 0.32 | 7 | 7 | 14 | 0.01109 | 0.001109 | 0.044362 | 0.044362 | 0.089833 | 2.5 | 2.5668 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.081336 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.166 | 100 | 100 | 95.5411 | 94.3752 | frequent cleaning/flush tank
42 | 10-11 | 10 | 11 | 183 | 2.1333 | 0.21333 | 17.28 | 56 | 0.30857 | 6 | 0 | 6 | 0.0047531 | 0.00047531 | 0.019012 | 0.019012 | 0.0385 | 2.5 | 1.6803 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.034858 | 0.05 | 0.0375 | 0.25 | 0.625 | 0.81129 | 100 | 100 | 96.1042 | 95.2929 | frequent cleaning/flush tank
43 | 11-12 | 11 | 12 | 34 | 2.1333 | 0.21333 | 17.28 | 56 | 0.30857 | 6 | 6 | 12 | 0.0095061 | 0.00095061 | 0.038025 | 0.038025 | 0.077 | 2.5 | 2.3763 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.069716 | 0.075 | 0.05625 | 0.25 | 0.625 | 0.15073 | 100 | 100 | 95.2929 | 95.1421 | frequent cleaning/flush tank
FOR LATERALS |  |  |  |  | 0 | 0 | 0 |  | #DIV/0!
44 | 2-3 | 2 | 3 | 286 | 2.1333 | 0.21333 | 17.28 | 49 | 0.35265 | 6 | 0 | 6 | 0.0047531 | 0.00047531 | 0.019012 | 0.019012 | 0.0385 | 2.5 | 1.6803 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.034858 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.2679 | 100 | 100 | 96.1042 | 94.8362 | flush tank
45 | 4-5 | 4 | 5 | 144 | 0.71111 | 0.071111 | 5.76 | 21 | 0.27429 | 2 | 0 | 2 | 0.0015844 | 0.00015844 | 0.0063374 | 0.0063374 | 0.012833 | 2.5 | 0.97014 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.011619 | 0.05 | 0.0375 | 0.25 | 0.625 | 0.63839 | 100 | 100 | 96.1042 | 95.4658 | flush tank
46 | 37-38 | 37 | 38 | 549 | 3.2 | 0.32 | 25.92 | 77 | 0.33662 | 9 | 0 | 9 | 0.0071296 | 0.00071296 | 0.028518 | 0.028518 | 0.05775 | 2.5 | 2.058 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.052287 | 0.075 | 0.05625 | 0.25 | 0.625 | 2.4339 | 100 | 100 | 96.1042 | 93.6703 | flush tank
47 | 22-23 | 22 | 23 | 286 | 3.9111 | 0.39111 | 31.68 | 98 | 0.32327 | 11 | 0 | 11 | 0.008714 | 0.0008714 | 0.034856 | 0.034856 | 0.070583 | 2.5 | 2.2752 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.063907 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.2679 | 100 | 100 | 96.1042 | 94.8362 | flush tank
48 | 24-25 | 24 | 25 | 285 | 1.7778 | 0.17778 | 14.4 | 42 | 0.34286 | 5 | 0 | 5 | 0.0039609 | 0.00039609 | 0.015844 | 0.015844 | 0.032083 | 2.5 | 1.5339 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.029049 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.2635 | 100 | 100 | 96.1042 | 94.8407 | flush tank
49 | 27-30 | 27 | 30 | 262 | 2.1333 | 0.21333 | 17.28 | 50 | 0.3456 | 6 | 0 | 6 | 0.0047531 | 0.00047531 | 0.019012 | 0.019012 | 0.0385 | 2.5 | 1.6803 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.034858 | 0.05 | 0.0375 | 0.25 | 0.625 | 1.1615 | 100 | 100 | 96.1042 | 94.9426 | flush tank
50 | 26-31 | 26 | 31 | 278 | 3.2 | 0.32 | 25.92 | 78 | 0.33231 | 9 | 0 | 9 | 0.0071296 | 0.00071296 | 0.028518 | 0.028518 | 0.05775 | 2.5 | 2.058 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.052287 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.2325 | 100 | 100 | 96.1042 | 94.8717 | flush tank
51 | 39-49 | 39 | 49 | 322 | 3.2 | 0.32 | 25.92 | 84 | 0.30857 | 9 | 0 | 9 | 0.0071296 | 0.00071296 | 0.028518 | 0.028518 | 0.05775 | 2.5 | 2.058 | 9 | 0 | 1.75 | 0.0044333 | 1.1045 | 0.052287 | 0.075 | 0.05625 | 0.25 | 0.625 | 1.4275 | 100 | 100 | 96.1042 | 94.6766 | flush tank
[27 empty] | q/Q | d/D | v/V
[27 empty] | 0 | 0.05 | 0.2
[27 empty] | 0.05 | 0.075 | 0.25
[27 empty] | 0.1 | 0.25 | 0.55
[27 empty] | 0.15 | 0.3 | 0.6
[27 empty] | 0.2 | 0.35 | 0.65
[27 empty] | 0.25 | 0.4 | 0.7
[27 empty] | 0.3 | 0.425 | 0.725
[27 empty] | 0.35 | 0.45 | 0.75
[27 empty] | 0.4 | 0.5 | 0.8
[27 empty] | 0.45 | 0.525 | 0.825
[27 empty] | 0.5 | 0.55 | 0.85
[27 empty] | 0.55 | 0.6 | 0.875
[27 empty] | 0.6 | 0.625 | 0.9
[27 empty] | 0.65 | 0.65 | 0.925
[27 empty] | 0.7 | 0.7 | 0.95
[27 empty] | 0.75 | 0.725 | 0.975
[27 empty] | 0.8 | 0.75 | 0.975
[27 empty] | 0.85 | 0.8 | 1
[27 empty] | 0.9 | 0.825 | 1.25
[27 empty] | 0.95 | 0.875 | 1.25
[27 empty] | 1 | 0.925 | 1.5
[10 empty] | 16: ID; 17: Label; 18: Elevation (Ground) (ft); 19: Set Rim to Ground Elevation?; 20: Elevation (Rim) (ft); 21: Bolted Cover?; 22: Elevation (Invert) (ft); 23: Inflow (Wet) Collection; 24: Flow (Total In) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | Sanitary Loads | Notes
[10 empty] | 16: 31; 17: MH-1; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 32; 17: MH-2; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 33; 17: MH-3; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.81; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 34; 17: MH-4; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 35; 17: MH-5; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.13; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 36; 17: MH-6; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 37; 17: MH-7; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 95.54; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 38; 17: MH-8; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 92.47; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 39; 17: MH-9; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 40; 17: MH-10; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 41; 17: MH-11; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 95.29; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 42; 17: MH-12; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.83; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 43; 17: MH-13; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 44; 17: MH-14; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.81; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 45; 17: MH-15; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 93.95; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 46; 17: MH-16; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 93.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 47; 17: MH-17; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 48; 17: MH-18; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.33; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 49; 17: MH-19; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 92.11; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 50; 17: MH-20; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 51; 17: MH-21; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.8; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 52; 17: MH-22; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 53; 17: MH-23; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.06; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 54; 17: MH-24; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 55; 17: MH-25; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 93.24; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 56; 17: MH-26; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 57; 17: MH-27; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 58; 17: MH-28; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 59; 17: MH-29; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.92; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 60; 17: MH-30; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.2; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 61; 17: MH-31; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 93.51; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 62; 17: MH-32; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 92.32; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 63; 17: MH-33; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 91.09; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 64; 17: MH-34; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 87.58; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 65; 17: MH-35; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 85.17; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 66; 17: MH-36; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 83.45; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 67; 17: MH-37; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 68; 17: MH-38; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 82.76; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 69; 17: MH-39; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 70; 17: MH-40; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 71; 17: MH-41; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.11; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 72; 17: MH-42; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 92.19; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 73; 17: MH-43; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 74; 17: MH-44; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 95.44; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 75; 17: MH-45; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.69; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 76; 17: MH-46; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 96.1; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 77; 17: MH-47; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 94.17; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 78; 17: MH-48; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 92.69; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 79; 17: MH-49; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 91.7; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 80; 17: MH-50; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 82.05; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: 81; 17: MH-51; 18: 100; 19: TRUE; 20: 100; 21: FALSE; 22: 81.06; 23: <Collection: 0 items>; 24: (N/A); 25: Flow (Total Out) (cfs); 26: Depth (Out) (ft); 27: Hydraulic Grade Line (Out) (ft); 28: Headloss Method; 29: Hydraulic Grade Line (In) (ft); 30: Is Ever Overflowing? | Is Overflowing? | <Collection: 1 item>
[10 empty] | 16: ID; 17: Label; 18: Start Node; 19: Set Invert to Start?; 20: Invert (Start) (ft); 21: Stop Node; 22: Set Invert to Stop?; 23: Invert (Stop) (ft); 24: Has User Defined Length?; 25: Length (User Defined) (ft); 26: Length (Scaled) (ft); 27: Slope (Calculated) (ft/ft); 28: Section Type; 29: Diameter (in); 30: Manning's n | Flow (Middle) (cfs) | Velocity (ft/s) | Depth (Middle) (ft) | Capacity (Full Flow) (cfs) | Flow / Capacity (Design) (%) | Depth/Rise (%) | Notes
[10 empty] | 16: 82; 17: CO-1; 18: MH-1; 19: TRUE; 20: 96.1; 21: MH-3; 22: FALSE; 23: 94.81; 24: FALSE; 26: 73.7; 27: 0.018; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.73 | (N/A) | (N/A)
[10 empty] | 16: 83; 17: CO-2; 18: MH-3; 19: TRUE; 20: 94.81; 21: MH-5; 22: FALSE; 23: 94.13; 24: FALSE; 26: 57.7; 27: 0.012; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.86 | (N/A) | (N/A)
[10 empty] | 16: 84; 17: CO-3; 18: MH-5; 19: TRUE; 20: 94.13; 21: MH-8; 22: FALSE; 23: 92.47; 24: FALSE; 26: 112.6; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.32 | (N/A) | (N/A)
[10 empty] | 16: 85; 17: CO-4; 18: MH-8; 19: TRUE; 20: 92.47; 21: MH-36; 22: FALSE; 23: 90.02; 24: FALSE; 26: 162.9; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.37 | (N/A) | (N/A)
[10 empty] | 16: 86; 17: CO-5; 18: MH-36; 19: TRUE; 20: 83.45; 21: MH-38; 22: FALSE; 23: 82.76; 24: FALSE; 26: 93.4; 27: 0.007; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.05 | (N/A) | (N/A)
[10 empty] | 16: 87; 17: CO-6; 18: MH-38; 19: TRUE; 20: 82.76; 21: MH-50; 22: FALSE; 23: 82.3; 24: FALSE; 26: 59.6; 27: 0.008; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.14 | (N/A) | (N/A)
[10 empty] | 16: 89; 17: CO-8; 18: MH-43; 19: TRUE; 20: 96.1; 21: MH-44; 22: FALSE; 23: 95.44; 24: FALSE; 26: 44.4; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.36 | (N/A) | (N/A)
[10 empty] | 16: 90; 17: CO-9; 18: MH-44; 19: TRUE; 20: 95.44; 21: MH-45; 22: FALSE; 23: 94.69; 24: FALSE; 26: 53.5; 27: 0.014; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.2 | (N/A) | (N/A)
[10 empty] | 16: 91; 17: CO-10; 18: MH-45; 19: TRUE; 20: 94.69; 21: MH-48; 22: FALSE; 23: 92.69; 24: FALSE; 26: 133.6; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.37 | (N/A) | (N/A)
[10 empty] | 16: 92; 17: CO-11; 18: MH-48; 19: TRUE; 20: 92.69; 21: MH-49; 22: FALSE; 23: 91.71; 24: FALSE; 26: 64; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.4 | (N/A) | (N/A)
[10 empty] | 16: 93; 17: CO-12; 18: MH-49; 19: TRUE; 20: 91.7; 21: MH-50; 22: FALSE; 23: 90.07; 24: FALSE; 26: 136; 27: 0.012; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.91 | (N/A) | (N/A)
[10 empty] | 16: 94; 17: CO-13; 18: MH-6; 19: TRUE; 20: 96.1; 21: MH-7; 22: FALSE; 23: 95.54; 24: FALSE; 26: 41.8; 27: 0.013; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.14 | (N/A) | (N/A)
[10 empty] | 16: 95; 17: CO-14; 18: MH-7; 19: TRUE; 20: 95.54; 21: MH-8; 22: FALSE; 23: 94.38; 24: FALSE; 26: 74.1; 27: 0.016; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.47 | (N/A) | (N/A)
[10 empty] | 16: 96; 17: CO-15; 18: MH-17; 19: TRUE; 20: 96.1; 21: MH-18; 22: FALSE; 23: 94.33; 24: FALSE; 26: 126.2; 27: 0.014; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.23 | (N/A) | (N/A)
[10 empty] | 16: 97; 17: CO-16; 18: MH-18; 19: TRUE; 20: 94.33; 21: MH-19; 22: FALSE; 23: 93.43; 24: FALSE; 26: 55.9; 27: 0.016; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.51 | (N/A) | (N/A)
[10 empty] | 16: 98; 17: CO-17; 18: MH-19; 19: TRUE; 20: 92.11; 21: MH-35; 22: FALSE; 23: 91.06; 24: FALSE; 26: 72.1; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.3 | (N/A) | (N/A)
[10 empty] | 16: 101; 17: CO-19; 18: MH-9; 19: TRUE; 20: 96.1; 21: MH-12; 22: FALSE; 23: 94.83; 24: FALSE; 26: 83.5; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.4 | (N/A) | (N/A)
[10 empty] | 16: 102; 17: CO-20; 18: MH-12; 19: TRUE; 20: 94.83; 21: MH-16; 22: FALSE; 23: 93.1; 24: FALSE; 26: 112.9; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.41 | (N/A) | (N/A)
[10 empty] | 16: 103; 17: CO-21; 18: MH-16; 19: TRUE; 20: 93.1; 21: MH-19; 22: FALSE; 23: 92.11; 24: FALSE; 26: 75.6; 27: 0.013; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.07 | (N/A) | (N/A)
[10 empty] | 16: 104; 17: CO-22; 18: MH-10; 19: TRUE; 20: 96.1; 21: MH-11; 22: FALSE; 23: 95.29; 24: FALSE; 26: 81.9; 27: 0.01; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.55 | (N/A) | (N/A)
[10 empty] | 16: 105; 17: CO-23; 18: MH-11; 19: TRUE; 20: 95.29; 21: MH-12; 22: TRUE; 23: 94.83; 24: FALSE; 26: 37.6; 27: 0.012; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.94 | (N/A) | (N/A)
[10 empty] | 16: 106; 17: CO-24; 18: MH-13; 19: TRUE; 20: 96.1; 21: MH-14; 22: FALSE; 23: 94.81; 24: FALSE; 26: 81.2; 27: 0.016; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.5 | (N/A) | (N/A)
[10 empty] | 16: 107; 17: CO-25; 18: MH-14; 19: TRUE; 20: 94.81; 21: MH-15; 22: FALSE; 23: 93.95; 24: FALSE; 26: 58.4; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.31 | (N/A) | (N/A)
[10 empty] | 16: 108; 17: CO-26; 18: MH-15; 19: TRUE; 20: 93.95; 21: MH-16; 22: FALSE; 23: 93.13; 24: FALSE; 26: 56.4; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.31 | (N/A) | (N/A)
[10 empty] | 16: 109; 17: CO-27; 18: MH-20; 19: TRUE; 20: 96.1; 21: MH-21; 22: FALSE; 23: 94.8; 24: FALSE; 26: 83.3; 27: 0.016; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.46 | (N/A) | (N/A)
[10 empty] | 16: 110; 17: CO-28; 18: MH-21; 19: TRUE; 20: 94.8; 21: MH-23; 22: FALSE; 23: 94.06; 24: FALSE; 26: 52.1; 27: 0.014; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.24 | (N/A) | (N/A)
[10 empty] | 16: 111; 17: CO-29; 18: MH-23; 19: TRUE; 20: 94.06; 21: MH-25; 22: FALSE; 23: 93.24; 24: FALSE; 26: 59.8; 27: 0.014; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.15 | (N/A) | (N/A)
[10 empty] | 16: 112; 17: CO-30; 18: MH-25; 19: TRUE; 20: 93.24; 21: MH-34; 22: FALSE; 23: 92.68; 24: FALSE; 26: 37.6; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.38 | (N/A) | (N/A)
[10 empty] | 16: 113; 17: CO-31; 18: MH-34; 19: TRUE; 20: 87.58; 21: MH-35; 22: FALSE; 23: 85.42; 24: FALSE; 26: 147.5; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.31 | (N/A) | (N/A)
[10 empty] | 16: 114; 17: CO-32; 18: MH-35; 19: TRUE; 20: 85.17; 21: MH-36; 22: FALSE; 23: 83.7; 24: FALSE; 26: 151.4; 27: 0.01; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.51 | (N/A) | (N/A)
[10 empty] | 16: 115; 17: CO-33; 18: MH-28; 19: TRUE; 20: 96.1; 21: MH-29; 22: FALSE; 23: 94.92; 24: FALSE; 26: 82.6; 27: 0.014; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.27 | (N/A) | (N/A)
[10 empty] | 16: 116; 17: CO-34; 18: MH-29; 19: TRUE; 20: 94.92; 21: MH-30; 22: FALSE; 23: 94.2; 24: FALSE; 26: 48.7; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.31 | (N/A) | (N/A)
[10 empty] | 16: 117; 17: CO-35; 18: MH-30; 19: TRUE; 20: 94.2; 21: MH-31; 22: FALSE; 23: 93.51; 24: FALSE; 26: 43.1; 27: 0.016; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.51 | (N/A) | (N/A)
[10 empty] | 16: 118; 17: CO-36; 18: MH-31; 19: TRUE; 20: 93.51; 21: MH-32; 22: FALSE; 23: 92.32; 24: FALSE; 26: 81.9; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.3 | (N/A) | (N/A)
[10 empty] | 16: 119; 17: CO-37; 18: MH-32; 19: TRUE; 20: 92.32; 21: MH-33; 22: FALSE; 23: 91.09; 24: FALSE; 26: 83.9; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.32 | (N/A) | (N/A)
[10 empty] | 16: 120; 17: CO-38; 18: MH-33; 19: TRUE; 20: 91.09; 21: MH-34; 22: FALSE; 23: 87.58; 24: FALSE; 26: 235.8; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.34 | (N/A) | (N/A)
[10 empty] | 16: 121; 17: CO-39; 18: MH-40; 19: TRUE; 20: 96.1; 21: MH-41; 22: FALSE; 23: 94.11; 24: FALSE; 26: 132.2; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.38 | (N/A) | (N/A)
[10 empty] | 16: 122; 17: CO-40; 18: MH-41; 19: TRUE; 20: 94.11; 21: MH-42; 22: FALSE; 23: 92.19; 24: FALSE; 26: 138.3; 27: 0.014; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.19 | (N/A) | (N/A)
[10 empty] | 16: 123; 17: CO-41; 18: MH-42; 19: TRUE; 20: 92.19; 21: MH-49; 22: FALSE; 23: 91.7; 24: FALSE; 26: 69; 27: 0.007; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.02 | (N/A) | (N/A)
[10 empty] | 16: 125; 17: CO-42; 18: MH-46; 19: TRUE; 20: 96.1; 21: MH-47; 22: FALSE; 23: 94.17; 24: FALSE; 26: 128.6; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.37 | (N/A) | (N/A)
[10 empty] | 16: 126; 17: CO-43; 18: MH-47; 19: TRUE; 20: 94.17; 21: MH-48; 22: FALSE; 23: 93.48; 24: FALSE; 26: 46.8; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.32 | (N/A) | (N/A)
[10 empty] | 16: 127; 17: CO-44; 18: MH-50; 19: TRUE; 20: 82.05; 21: MH-51; 22: FALSE; 23: 81.06; 24: FALSE; 26: 160.2; 27: 0.006; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 2.8 | (N/A) | (N/A)
[10 empty] | 16: 133; 17: CO-45; 18: MH-2; 19: TRUE; 20: 96.1; 21: MH-3; 22: FALSE; 23: 94.84; 24: FALSE; 26: 75.1; 27: 0.017; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.63 | (N/A) | (N/A)
[10 empty] | 16: 134; 17: CO-46; 18: MH-4; 19: TRUE; 20: 96.1; 21: MH-5; 22: FALSE; 23: 95.47; 24: FALSE; 26: 42.8; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.35 | (N/A) | (N/A)
[10 empty] | 16: 135; 17: CO-47; 18: MH-37; 19: TRUE; 20: 96.1; 21: MH-38; 22: FALSE; 23: 93.67; 24: FALSE; 26: 159.5; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.4 | (N/A) | (N/A)
[10 empty] | 16: 136; 17: CO-48; 18: MH-39; 19: TRUE; 20: 96.1; 21: MH-49; 22: FALSE; 23: 94.68; 24: FALSE; 26: 112.4; 27: 0.013; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.01 | (N/A) | (N/A)
[10 empty] | 16: 137; 17: CO-49; 18: MH-24; 19: TRUE; 20: 96.1; 21: MH-25; 22: FALSE; 23: 94.84; 24: FALSE; 26: 82.7; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.4 | (N/A) | (N/A)
[10 empty] | 16: 138; 17: CO-50; 18: MH-22; 19: TRUE; 20: 96.1; 21: MH-23; 22: FALSE; 23: 94.84; 24: FALSE; 26: 82.7; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.41 | (N/A) | (N/A)
[10 empty] | 16: 139; 17: CO-51; 18: MH-26; 19: TRUE; 20: 96.1; 21: MH-31; 22: FALSE; 23: 94.87; 24: FALSE; 26: 84.5; 27: 0.015; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.3 | (N/A) | (N/A)
[10 empty] | 16: 140; 17: CO-52; 18: MH-27; 19: TRUE; 20: 96.1; 21: MH-30; 22: FALSE; 23: 94.94; 24: FALSE; 26: 83.3; 27: 0.014; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 4.21 | (N/A) | (N/A)
[10 empty] | 16: 211; 17: CO-53; 18: MH-51; 19: TRUE; 20: 81.06; 21: O-1; 22: FALSE; 23: 80.81; 24: FALSE; 26: 34.4; 27: 0.007; 28: Circle; 29: 12; 30: 0.013 | (N/A) | (N/A) | (N/A) | 3.07 | (N/A) | (N/A)
OUTFALL
[21 empty] | ID | Label | Elevation (Ground) (ft) | Set Rim to Ground Elevation? | Elevation (Invert) (ft) | Boundary Condition Type | Boundary Element | Elevation (User Defined Tailwater) (ft) | Elevation-Flow Curve | Time-Elevation Curve | Cyclic Time-Elevation Curve | Tidal Gate? | Hydraulic Grade (ft) | Flow (Total Out) (cfs) | Notes
[21 empty] | 210 | O-1 | 100 | TRUE | 70 | Free Outfall |  |  | <Collection: 0 items> | <Collection: 0 items> | <Collection: 0 items> | FALSE | (N/A) | (N/A)